## 2100-XX Communications Messages

Data Format and Baud Rates

Data format = 8 bits, no parity, 1 stop bit.

Baud Rates 2400,4800,9600 (default) set by dip switches/links on the station.

Single Master, Multi Slave, the stations will only send messages when they have received a message from the Master (i.e computer or PLC device).

# Characters used and their ASCII values

| @ | 40h | Start Char |
| --- | --- | --- |
| : | 3Ah | End of message frame |
| <sp> | 20h | Data Separator (space) |
| <CR> | 0dh | End of Message Indicator |
| NN | 30-39h,41-46h | Station Number BCD |
| YY | 30-39h,41-46h | BCC Checksum Value HEX |
| XX | 30-39h,41-46h | 2 Digit Data Value HEX (MSB first) |
| XXXX | 30-39h,41-46h | 4 Digit Data Value HEX (MSB first) |
| FFFFFFFF | 30-39h,41-46h | IEEE Floating Point Number |
| , | 2Ch | Data Separator |

# Message format

Start Char = @

Station Number = nn (BCD number from 00 to 64)

Message Contents (Command)

End of message marker : (colon)

BCC 2 digit hex number giving checksum of message

End of message char = CR (0dh)

Example – read digital inputs from station 1

@01EX<sp>DI:XX<cr>

Response

@01EX<sp>DI<sp>0010<sp>0000<sp>0000:yy<cr>

The Station number is set using the Station Program Address dialog box. All stations are default to station 1 at the factory. If more than one station is on the loop they must all be given unique addresses before reading data out of the stations.

BCC calculation range and calculation method.

The BCC is calculated by adding the ascii characters in the data stream from the start of the station number upto and including the colon character “:” (8 bit addition, carry ignored).  The BCC is generated in the station and appended to the response message in the same way.

The station number is programmed into the unit using the station programming dialog boxes. Each station on the data loop uses a unique station number.

Station LEDS.

| RX | Flashes when the station receives serial characters |
| --- | --- |
| TX | Flashes indicating the station has understood the message and is sending a reply. |
| TXE | Flashes indicating the RS422 or 485 transmitter has turned on. There may be delays between the receipt of the RX data and the lighting of the TXE and TX lights depending on the setting of the TX and TXE delays in the station’s advanced programming dialog boxes. |

## Individual Message Descriptions.

## EX DO – Write Digital Outputs

Writes States of Relay Outputs

Send Message

@NNEX<sp>DO<sp>XXXX<sp>XXXX:YY<CR>

Param1 – digital outputs on station

XXXX=b15b14b13b12 b11b10b9b8 b7b6b5b4 b3b2b1b0

b0=Relay 1	A16,A4,A4e,AO,2100-D

b1=Relay 2	A16,A4,A4e,AO,2100-D

b2=Relay 3	A4,A4e,2100-D

b3=Relay 4 	A4,A4e,2100-D

b4=Relay 5 	A4e,2100-D

b5=Relay 6 	A4e,2100-D

b6=Relay 7 	A4e,2100-D

b7=Relay 8 	A4e,2100-D

b8=Relay 9	2100-D

b9=Relay 10	2100-D

b10=Relay 11	2100-D

b11=Relay 12	2100-D

All other bits zero

The States of the onboard relays of the station can be read using the EX DI command, param1.

Param2 – digital outputs on 2100-R

XXXX=b15b14b13b12 b11b10b9b8 b7b6b5b4 b3b2b1b0

b0	Relay 1 State		b1 	Relay 2 State

b2	Relay 3 State		b3	Relay 4 State

b4	Relay 5 State		b5	Relay 6 State

b6	Relay 7 State		b7	Relay 8 State

b8	Relay 9 State		b9	Relay 10 State

b10	Relay 11 State		b11	Relay 12 State

b12	Relay 13 State		b13	Relay 14 State

b14	Relay 15 State		b15	Relay 16 State

The States of the 2100-R relays of the station can be read using the EX DI command, param3.

Both params are specified even if a 2100-R is not fitted.

Reply Message

@NNOK:YY<CR>

Indicating successful write

To Write individual bits, a cached copy of the current states of the digital outputs must be read from the station using the EX DI command and then the bits are modified accordingly and written out using the EX DO command.

Any internal function on the station will override the states of the relay written by the EX DO command. i.e Comms time out function on will always set Relay 2 when a valid comms command has been received. Station controllers will write the relay states every time the controller setpoints are checked (includes manual override modes).

## EX DI – Read Digital outputs and digital outputs

Reads States of Digital Inputs and Digital Outputs

Send Message

@NNEX<sp>DI:YY<CR>

A16,A4,A4e,AO Reply Message

@NNEX<sp>DI<sp>XXXX<sp>XXXX<sp>XXXX:YY<CR>

2100-D replies with

@NNEX<sp>DI<sp>XXXX<sp>XXXX:YY<CR>

Param1 – state of digital outputs

XXXX=b15b14b13b12 b11b10b9b8 b7b6b5b4 b3b2b1b0

b0=Relay 1	A16,A4,A4e,AO,2100-D

b1=Relay 2	A16,A4,A4e,AO,2100-D

b2=Relay 3	A4,A4e,2100-D

b3=Relay 4 	A4,A4e,2100-D

b4=Relay 5 	A4e,2100-D

b5=Relay 6 	A4e,2100-D

b6=Relay 7 	A4e,2100-D

b7=Relay 8 	A4e,2100-D

b8=Relay 9	2100-D

b9=Relay 10	2100-D

b10=Relay 11	2100-D

b11=Relay 12	2100-D

All other bits zero

Param2 – state of digital inputs

XXXX=b15b14b13b12 b11b10b9b8 b7b6b5b4 b3b2b1b0

b0	Digital Input 1 State

b1 	Digital Input 2 State

b2	Digital Input 3 State

b3	Digital Input 4 State (AO,A4, A16 Rev1 Only, A16 Rev0 returns 0)

b4	Digital Input 5 State (AO,2100-D only)

b5 	Digital Input 6 State (AO,2100-D only)

b6	Digital Input 7 State (AO,2100-D only)

b7	Digital Input 8 State (AO,2100-D only)

b8 	Digital Input 9 State (AO,2100-D only)

b9	Digital Input 10 State (AO,2100-D only)

b10	Digital Input 11 State (AO,2100-D only)

b11	Digital Input 12 State (AO,2100-D only)

All other bits zero

Param3 – state of 2100-R digital outputs.

XXXX=b15b14b13b12 b11b10b9b8 b7b6b5b4 b3b2b1b0

All three Params are returned even if a 2100-R is not fitted.

b0	Relay 1 State		b1 	Relay 2 State

b2	Relay 3 State		b3	Relay 4 State

b4	Relay 5 State		b5	Relay 6 State

b6	Relay 7 State		b7	Relay 8 State

b8	Relay 9 State		b9	Relay 10 State

b10	Relay 11 State		b11	Relay 12 State

b12	Relay 13 State		b13	Relay 14 State

b14	Relay 15 State		b15	Relay 16 State

A Bit Set/ Reset has to be synthesised by retaining the last value written and ANDING(reset) or ORING(set) a new value to create the bit set or reset.

## EX E5 – Read analogue inputs

Reads the States of the station analogue inputs (A16,A4,A4e,AO only)

Send Message

@NNEX<sp>E5<sp>XX:YY<CR>	read analogue inputs

@NNEX<sp>E5<sp>00:YY<CR>		read analogue inputs 1-4

@NNEX<sp>E5<sp>01:YY<CR>		read analogue inputs 5-8

@NNEX<sp>E5<sp>02:YY<CR>		read analogue inputs 9-12 (A16 only)

@NNEX<sp>E5<sp>03:YY<CR>		read analogue inputs 13-16 (A16 only)

Reply Message

@NNEX<sp>E5<sp>00<sp>ffffffff<sp>ffffffff<sp>ffffffff<sp>ffffffff:YY<CR>

@NNEX<sp>E5<sp>01<sp>ffffffff<sp>ffffffff<sp>ffffffff<sp>ffffffff:YY<CR>

@NNEX<sp>E5<sp>02<sp>ffffffff<sp>ffffffff<sp>ffffffff<sp>ffffffff:YY<CR>

@NNEX<sp>E5<sp>03<sp>ffffffff<sp>ffffffff<sp>ffffffff<sp>ffffffff:YY<CR>

ffffffff=IEEE float number giving value of input, ranged according to the input type selected. i.e

DCX range value = 0-100 %

RTD1 range value  = 0-25 Deg C (plus slight overrange at both ends)

RTD10 range value  = -200-250 Deg C (plus slight overrange at both ends)

IEEE Floating point format.

First ff = Byte 3

Second ff = Byte 2

Third ff = Byte 1

Fourth ff = Byte 0

Byte 3                              Byte 2                             Byte 1                         Byte 0

31 30 29 28 27 26 25 24.23 22 21 20 19 18 17 16.15 14 13 12 11 10 9 8.7 6 5 4 3 2 1 0

s  exponent                           mantissa

s=sign = bit 31

exponent=bits 22-30

mantissa=bits 0-21

Note:

The values returned by the EX E5 commands are the last values read from the inputs. Issuing a EX E5 command does not force the A16 to read in the channels requested at the time the command is issued.

## EX E6 – Read Ambient Sensor & misc

Send Message

@NNEX<sp>E6:YY<CR>	read data

Reply Message

@NNEX<sp>E6<sp>ffffffff<sp>XX<sp>XX<sp>XXXX<sp>XX<sp>XXXX<sp>XXXX<sp>XXXX:YY<CR>

Param1 ffffffff Ambient onboard sensor for cold junction compensation (See EX E5 fp format)

Param 2 XX Current Input being read (0-0f h)

Param 3 XX Current Muxltiplexer channel being read.

Param 4 XXXX reserved

Param 5 XX modeswitch (0-3fh)

Param 6 XXXX reserved

Param 7 XXXX reserved

Param 8 XXXX current rtx channel

## EX EN – Read Multiplexer Channels

EX En reads the 16 channels of each Multiplexer

@NNEX<sp>E1:YY<CR>		Read Multiplexer 1

@NNEX<sp>E2:YY<CR>		Read Multiplexer 2

@NNEX<sp>E3:YY<CR>		Read Multiplexer 3

@NNEX<sp>E4:YY<CR>		Read Multiplexer 4

Reply Message

@NNEX<sp>EN<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX<sp>XXX:YY<CR>

i.e EN=E1,E2,E3,E4.

Param1-Param 16 Values of channels 1-16, XXX = Hex 000-FFF 12 bit number.

## EX RO – Read Analogue Output Channels

The EX RO command reads the values of the analogue output channels.

@NNEX<sp>RO:YY<CR>

Reply Message

@NNEX<sp>RO<sp>XXXX<sp>XXXX<sp>XXXX<sp>XXXX:YY<CR>

Param1..Param4 values of analogue output channels 1-4 (three and four are not used).

XXXX=12 bit value 0000-0FFF, leading zero is set to zero.

EX RO=O=Letter O

## EX AO – Write Analogue Output Channels

The EX AO command writes the values of the analogue output channels.

@NNEX<sp>RO<sp>XXXX<sp>XXXX<sp>XXXX<sp>XXXX:YY<CR>

Reply Message

@NNOK:YY<CR>

Param1..Param4 values of analogue output channels 1-4 (three and four are not used).

XXXX=12 bit value 0000-0FFF, leading zero should be set to zero.

A cached copy of the output states must be kept for individual write to the analogue outputs.

If the Analogue outputs are assigned specific functions in the station other than general SCADA outputs then the values written by this command will be overwritten by the internal function in the station.

## EX WA – Write Single Analogue Output Channel 2100-AO only

The EX AO command writes the values of a single output channel.

@NNEX<sp>WA<sp>XX<sp>XXXX:YY<CR>

Reply Message

@NNOK:YY<CR>

Param 1 is output index 00=output1,01=output2 to 07=output 8

Param 2 value of analogue output channel.

XXXX=12 bit value 0000-0FFF, leading zero should be set to zero.

If the Analogue outputs are assigned specific functions in the station other than general SCADA outputs then the values written by this command will be overwritten by the internal function in the station.

## EX R1 – Read Analogue Output Channels 2100-AO only

The EX R1 command reads the values of the analogue output channels 5-8

@NNEX<sp>R1:YY<CR>

Reply Message

@NNEX<sp>R1<sp>XXXX<sp>XXXX<sp>XXXX<sp>XXXX:YY<CR>

Param1..Param4 values of analogue output channels 5-8.

XXXX=12 bit value 0000-0FFF, leading zero is set to zero.

EX R1=1=Number 1

## PS – Read Controller Data

This message reads the setup of the station controllers.

Number of controllers.

| Station | 2100-R not fitted | 2100-R fitted |
| --- | --- | --- |
| A16 | 2 Single Action, or 1 Dual Action controller | 16 Single Action or 8 Dual Action Controller |
| A4 | 4 Single Action or two Dual Action controllers. | 4 Single Action or 4 Dual Action controllers. |
| A4e | 4 Single Action or four Dual Action controllers. | 4 Single Action or 4 Dual Action controllers. |
| AO | 2 Single Action, or 1 Dual Action controller | N/A |

Send Message

@NNPS<sp>XX:YY<CR>	read data

Reply Message

@NNPS<sp>XX,XXXXffffffffffffffff:YY<CR>

XX=Controller index, =10d*controller number-1

i.e 00=controller 1, 0a=controller 2, 14=controller 3

Param1=XXXX controller flags

Param2=ffffffff setpoint (IEEE Number)

Param3=ffffffff differential (IEEE Number)

# Controller flags

SA= Single Action, DA= Dual Action. Set by the Controller mode in the Station Advanced Dialog box.

| Bit | Function | SA/DA Mode | Value = 0 | Value =1 |
| --- | --- | --- | --- | --- |
| b0 | Enable | Both | Controller Disabled | Controller Enabled |
| b1 | Manual Override | Both | Auto Mode | Manual Mode. Output State Specified by Bit 2 (SA) or bits 5,6 (DA). |
| b2 | Manual State | SA | Output Off | Output On |
| b3 | Reverse Action | Both | Heating Action (Relay is on when heating required i.e when temp is below setpoint) | Cooling Action (Relay is on when cooling is required i.e when temp is above setpoint). |
| b4 | Heat Cool Mode | DA | Single action control with either one of Heating or Cooling control specified by Reverse Action Bit | Dual Action mode with both Heat and Cool relays working. |
| b5 | Manual Heat On | DA | Heat Relay Off when manual override set | Heat Relay On when manual override set. (Only one of bit 5 and bit 6 should be set at one time) |
| b6 | Manual Cool On | DA | Cool Relay Off when manual override set | Cool Relay On when manual override set. (Only one of bit 5 and bit 6 should be set at one time) |

Other bits are reserved and should be set to zero.

If a controller is active and then deactivated by clearing the the controllers enable bit, the controllers relay state will be left in the last remaining state. It is up to the software to turn the relay to the desired state.

# Controller Modes

Single Action/Dual Action.

The Single Action/Dual Action mode is specified in the Station’s Advanced dialog box. Details of relay allocations are specified in the manual supplied with the station. In the Single Action Mode the behaviour of the relays is defined by the control action chosen. In the Dual Action mode, the functions of the relays are fixed, but will only operate according to the control action chosen.

# Dual Action Mode Relays

| Relay | Function | Heating | Cooling | Heat/Cool |
| --- | --- | --- | --- | --- |
| Relay 1 | Heat Action | Active | Off | Active |
| Relay 2 | Cool Action | Off | Active | Active |

This is chosen so the user can switch between Heat/Cool and Heat only or Cool only and have the relay numbers stay the same.

# A16

For the Single Action control mode there are 16 controllers.

For the Dual Action mode, there are 8 controllers. With the setup for the extra parameters needed for the controller coming from the controller index+8.

# A16 Dual Action Summary

| Controller | Index | Controller Flags | Setpoint | Differential |
| --- | --- | --- | --- | --- |
| 1 | 00 | As Required | Controller 1 Setpoint | Controller 1 Cool Differential |
| 2 | 0A | As Required | Controller 2 Setpoint | Controller 2 Cool Differential |
| 3 | 14 | As Required | Controller 3 Setpoint | Controller 3 Cool Differential |
| 4 | 1E | As Required | Controller 4 Setpoint | Controller 4 Cool Differential |
| 5 | 28 | As Required | Controller 5 Setpoint | Controller 5 Cool Differential |
| 6 | 32 | As Required | Controller 6 Setpoint | Controller 6 Cool Differential |
| 7 | 3C | As Required | Controller 7 Setpoint | Controller 7 Cool Differential |
| 8 | 46 | As Required | Controller 8 Setpoint | Controller 8 Cool Differential |
| 9 | 50 | 0 | Controller 1 Deadband | Controller 1 Heat Differential |
| 10 | 5A | 0 | Controller 2 Deadband | Controller 2 Heat Differential |
| 11 | 64 | 0 | Controller 3 Deadband | Controller 3 Heat Differential |
| 12 | 6E | 0 | Controller 4 Deadband | Controller 4 Heat Differential |
| 13 | 78 | 0 | Controller 5 Deadband | Controller 5 Heat Differential |
| 14 | 82 | 0 | Controller 6 Deadband | Controller 6 Heat Differential |
| 15 | 8C | 0 | Controller 7 Deadband | Controller 7 Heat Differential |
| 16 | 96 | 0 | Controller 8 Deadband | Controller 8 Heat Differential |

Index=(Controller number-1)*10d

# A4/A4e

For the Single Action control mode there are 4 controllers.

For the Dual Action mode, there are 4 controllers. With the setup for the extra parameters needed for the controller coming from the controller index+4.

# A4 Dual Action Summary

| Controller | Index | Controller Flags | Setpoint | Differential |
| --- | --- | --- | --- | --- |
| 1 | 00 | As Required | Controller 1 Setpoint | Controller 1 Cool Differential |
| 2 | 0A | As Required | Controller 2 Setpoint | Controller 2 Cool Differential |
| 3 | 14 | As Required | Controller 3 Setpoint | Controller 3 Cool Differential |
| 4 | 1E | As Required | Controller 4 Setpoint | Controller 4 Cool Differential |
| 5 | 28 | 0 | Controller 1 Deadband | Controller 1 Heat Differential |
| 6 | 32 | 0 | Controller 2 Deadband | Controller 2 Heat Differential |
| 7 | 3C | 0 | Controller 3 Deadband | Controller 3 Heat Differential |
| 8 | 46 | 0 | Controller 4 Deadband | Controller 4 Heat Differential |

Index=(Controller number-1)*10d

## PS – Write Controller Data

Send Message

@NNPS<sp>XX,XXXXffffffffffffffff:YY<CR>	send data

XX=Controller index, =10d*controller number-1

i.e 00=controller 1, 0a=controller 2, 14=controller 3

Param1=XXXX controller flags

Param2=ffffffff setpoint (IEEE Number)

Param3=ffffffff differential (IEEE Number)

Reply Data

@NNPS<sp>XX,XXXXffffffffffffffff:YY<CR>

The reply data is the same as one for a read of the controller data and can be used to verify the data has been written correctly.

The Message is the same as the Read Controller Data message, but instead of the “:” indicating the end of message after the controller index, the “,” indicates write data is to follow.

Note

1. Always check controller write data with the supporting dialog boxes in the Station Setup to check the data has been written to the correct locations.

2. Be aware of the EEPROM endurance limit of 10,000 writes per eeprom word. Try to restrict changes to controller setpoints if possible. EEPROM performance after 10,000 writes is not guaranteed (HC11E9 EEPROM limitation).

## Sample C Routines

## Convert a floating point number to a string

//For Writing a float value to the station

//put the float value into the buffer string

void ConvertFloatToIEEE(float fvalue,char *buffer)

{

unsigned char *ptr;

//point to the beginning of the float value

ptr=(unsigned char *)&fvalue;

//get the data bytes from the float value and put them in the string, //starting with byte 3

sprintf(buffer,"%02X%02X%02X%02X",*(ptr+3)&255,*(ptr+2)&255,*(ptr+1)&255,*(ptr+0)&255);

}

## Convert the string to a floating point number

//for converting a float value in the string into a float number

float ConvertIEEEToFloat(char * pData)

{

float fvalue;

int count;

int i;

unsigned char *cptr;

//error check

//dont let the data if all chars in the string are 'F', it is an //invalid number

for (i=0,count=0;i<8;i++)

if (*(pData+i)=='F')

count++;

else break;

if (count==8)

return 0;

fvalue=0;

//point to the float value

cptr=(unsigned char *)&fvalue;

//start with byte 3

cptr+=3;

//four bytes to di

count=4;

while(count)

{

//get the data from the string

sscanf(pData,"%02X",&i);

//store it

*cptr=i&255;

//move to the next byte

count--;

lpData+=2;

cptr--;

}

return (float)fvalue;

}

## Calculate a BCC value and append it to a message

Message =@NN…….:

void AddBCCToMessage(char *message)

{

PSTR pData;

int bccvalue;

char endtext[10];

bccvalue=0;

pData=message+1;

while(*pData!='\0')

bccvalue+=(unsigned char)(*pData++)&255;

bccvalue&=255;

sprintf(endtext,"%02X\x00d",bccvalue);

strcat(message,endtext);

}

## Note on Serial Communications

In order to accomplish successful communications the following is recommended.

Generate a BCC on the sent data.

Always check the BCC on the reply data and throw the message away if the calculated value is different from the value in the receive string.

If any framing,overrun or other receive errors occur, throw the message away and send a new message.

Do not assume the first replied character will be a @. Rubbish characters can always occur, so start assembling a receive string when the @ is detected.

Decode the reply message when the <CR> has arrived, don’t use the : as an end of message marker.

Check the reply data is the same as you have sent i.e if sending EX DI, check the reply string has EX DI in it before decoding the data. I.e the send string is EX<sp>DI: and the reply is EX<sp>DI<sp>, the colon changes to a space in the reply.

Also check the station number in the reply string is correct in case another station is replying with data.

Make the time to wait for a reply message adjustable for use with radio installations if the reply message will take several seconds.

When writing data, use the Micro Scan station programming boxes to verify the data has been programmed to the correct locations. The Micro Scan Programming Station Address dialog box must be used to give each station a unique station number if more than one station is on the loop.